## Sheet1
| F4T Ramp Page Registers and 9099 Substitution Variable Names |  |  |  | 2017-07-08
Use these Substution Variables when creating Ramp or Cascade Control html pages.
Parameter Name | Range | Data Type and Access (R/W) | Modbus Registers | Name | Value | Sustitution Variables
Closed-Loop Set Point, CH 1 | -99,999 To 99,999 | IEEE Float R | 2810 |  |  | %CLCh1input%
Closed-Loop Set Point, CH 2 | -99,999 To 99,999 | IEEE Float R | 2970 |  |  | %CLCh2input%
Closed-Loop Set Point, CASCADE 1 | -99,999 To 99,999 | IEEE Float R | 4188 |  |  | %Cas1input%
Set Point, CASCADE 1 | -99,999 To 99,999 | IEEE Float R/W | 4042 | Cas1inputSP |  | %Cas1inputSP%
Cascade Outer Loop 1 (part temp) | -99,999 To 99,999 | IEEE Float R | 4180 |  |  | %OLPartinput%
Cascade Outer Loop 1 (air temp) | -99,999 To 99,999 | IEEE Float R | 4182 |  |  | %OLAirinput%
Outer Loop Set Point Closed | -99,999 To 99,999 | IEEE Float R | 2190 |  |  | %TBD%
Ramp Action, CH 1 | Off (62) | unsigned 16-bit, R/W | 2794 | Ramp1Act | Off | %Ramp1ActOff%
| Startup (88) |  |  | Ramp1Act | Startup | %Ramp1ActStart%
| Set Point (85) |  |  | Ramp1Act | SetPoint | %Ramp1ActSP%
| Both (13) |  |  | Ramp1Act | Both | %Ramp1ActBoth%
Ramp Scale, CH1 | Units/Minute = 57 | unsigned 16-bit, R/W | 2796 | Ramp1Units | Minutes | %Ramp1UnitsMin%
| Units/Hour) = 39 |  |  | Ramp1Units | Hours | %Ramp1UnitsHr%
Ramp Rate, CH1 | 0 to 99,999 | IEEE Float R/W | 2798 | Ramp1RateSP |  | %Ramp1RateSP%
Ramp Action, CH 2 | Off (62) | unsigned 16-bit, R/W | 2954 | Ramp2Act | Off | %Ramp1ActOff%
| Startup (88) |  |  | Ramp2Act | Startup | %Ramp2ActStart%
| Set Point (85) |  |  | Ramp2Act | SetPoint | %Ramp2ActSP%
| Both (13) |  |  | Ramp2Act | Both | %Ramp2ActBoth%
Ramp Scale, CH2 | Units/Minute = 57 | unsigned 16-bit, R/W | 2956 | Ramp2Units | Minutes | %Ramp2UnitsMin%
| Units/Hour) = 39 |  |  | Ramp2Units | Hours | %Ramp2UnitsHr%
Ramp Rate, CH2 | 0 to 99,999 | IEEE Float R/W | 2957 | Ramp2RateSP |  | %Ramp2RateSP%
Ramp Action, CASCADE 1 | Off (62) | unsigned 16-bit, R/W | 4054 | Ramp3Act | Off | %Ramp3ActOff%
| Startup (88) |  |  | Ramp3Act | Startup | %Ramp3ActStart%
| Set Point (85) |  |  | Ramp3Act | SetPoint | %Ramp3ActSP%
| Both (13) |  |  | Ramp3Act | Both | %Ramp3ActBoth%
Ramp Scale, CASCADE 1 | Units/Minute = 57 | unsigned 16-bit, R/W | 4056 | Ramp3Units | Minutes | %Ramp3UnitsMin%
| Units/Hour) = 39 |  |  | Ramp3Units | Hours | %Ramp3UnitsHr%
Ramp Rate, CASCADE 1 | 0 to 99,999 | IEEE Float R/W | 4058 | Ramp3RateSP |  | %Ramp3RateSP%